# TU-100 Trainer Emulator, UEERA0036, Project Brief

## Background

UEE32225 - Certificate III in Air Conditioning and Refrigeration.

UEERA0036 requires learners to establish and document the basic operating conditions of vapour compression refrigeration systems. Access to physical trainer units can be limited, and readings can vary depending on setup and conditions.

This project will deliver a browser based emulator of the TU-100 style refrigeration trainer so students and teachers can rehearse correct configuration, identify measurement points, and interpret pressures and temperatures before, during, and after hands on sessions.

## Problem Statement

We need an emulator that:

- represents the TU-100 trainer layout and key components clearly

- allows users to set the unit into valid operating configurations using valves

- generates believable gauge and clamp readings based on ambient temperature and refrigerant selection

- pauses, and explains why, when the valve configuration is invalid

- is simple enough to run on Github – Accessible via web

## Objectives

- Provide a reliable learning tool aligned to UEERA0036 measurement and interpretation tasks.

- Create a single page emulator that runs on desktop and tablet browsers.

- Support multiple refrigerants using the polynomial pressure models provided in the project logic.

- Use a clear, low friction UI that matches RMIT styling and is easy for low confidence users.

- Create documentation, including a glossary, to support onboarding and handover.

## Scope

In scope:

- Interactive valve panel with on, off states for HP1 to HP4, LRI, LRK, LRB, TXV, CTV, ACI, ACO, ACB.

- Mode selection, cooling and heating, including UI label swap of the two fin tube heat exchangers.

- Refrigerant selection for R134a, R290, R32, R454C.

- Ambient temperature input, Tamb, via slider.

- Output instrumentation including three pressure gauges, and temperature clamp readouts defined in the project logic.

- Truth table gating, emulator runs only for the eight valid configurations.

- Equation chain for pressures and temperatures, using assumed TD, SH, SC, and split values.

Out of scope for MVP:

Full thermodynamic simulation, mass flow modelling, compressor maps, or real time transients.

Automatic expansion valve, AXV, behaviour, it can appear in UI but is not simulated.

Fault simulation such as undercharge, overcharge, airflow restriction, or component failures.

Data export, LMS integration, or authentication.

## Users and stakeholders

Students, practising configuration and interpretation of readings.

Teachers, using the emulator as pre class and revision support.

RMIT Digital Media Design team, implementing and maintaining the build.

Course and cluster stakeholders supporting UEERA0036 delivery.

## Functional requirements

Inputs

Refrigerant dropdown with four options.

Mode selector, cooling or heating.

Tamb slider, in degrees Celsius, within the model range.

Valve toggles for the full set of trainer valves.

Validation, emulation gate

Detect whether valve states match one of the eight valid truth table configurations.

If invalid, outputs display as blank or placeholders, and a clear status message is shown.

AXV state is ignored by validation and calculations.

Outputs

Pressures, Pdis, Pevap, Psuc, displayed numerically and via gauge needles.

Temperatures, Tdis, Tco, Tlro, Teo, Tacco, Tsuc, Tamb, Tcondairo, Tevapairo.

Two airflow readouts as placeholders until validated with the physical unit.

## Non functional requirements

Runs in a modern browser using HTML, CSS, and JavaScript with no external dependencies required.

Responsive layout, usable on desktop and tablet.

Clear typography, adequate spacing, and accessible contrast for readability.

Maintainable code structure with constants and refrigerant models defined in one place.

## Solution overview

The emulator operates as a rule based model:

User selects refrigerant, mode, and Tamb, then sets valve states.

A truth table matcher checks whether the current valve pattern matches one valid configuration.

If matched, the model computes saturation temperatures from Tamb using assumed TD values.

Pressures are computed using refrigerant polynomial models, Pdew(T).

Temperatures at key points are derived using assumed superheat, subcool, and split values.

Results are rendered to the UI, and heating mode swaps coil labels only.

## Milestones

Define UI layout and component list, done in brief.

Build MVP emulator shell, valves, inputs, outputs.

Implement truth table gating and calculation engine.

Validate against physical TU-100 observations, tune constants and tentative offsets.

User testing with a teacher cohort, revise UI and copy.

Release and handover, including documentation and glossary.

## Roles and responsibilities

Lawrence, project lead, logic implementation, testing, stakeholder updates, deployment packaging.

Digital Media Design team, UI build, interaction design, styling, documentation.

Teaching staff, validation of terminology, expected behaviours, and learning alignment.

Program stakeholders, confirm delivery context and acceptance criteria.

## Glossary

| Term | Meaning |
| --- | --- |
| Tamb | Ambient air temperature around the trainer, used as the primary input for the model. |
| Mode, cooling | Configuration where one coil rejects heat to air, condenser, and the other absorbs heat, evaporator. |
| Mode, heating | Configuration where coil roles swap relative to cooling, in the emulator this is handled as a UI label swap. |
| Refrigerant | Working fluid that circulates through the system, carrying heat through phase change. |
| R134a, R290, R32, R454C | Refrigerant options supported by the emulator. Each uses a refrigerant specific pressure model. |
| Saturation temperature | Temperature where the refrigerant boils or condenses at a given pressure. |
| Dew point, Tdew | For blends, the saturation point where vapour begins condensing to liquid at a given pressure. |
| Bubble point, Tbubble | For blends, the saturation point where liquid begins boiling to vapour at a given pressure. |
| Pdew(T) | Polynomial model returning dew side saturation pressure in kPa from temperature in degrees Celsius. |
| Glide | Temperature range over which a blend changes phase, causing dew and bubble values to differ. |
| Pdis | Discharge, high side pressure, derived from condensing saturation temperature. |
| Pevap | Evaporator, low side pressure, derived from evaporating saturation temperature. |
| Psuc | Suction pressure at compressor inlet, derived from a slightly lower temperature than Tevap in the simplified model. |
| Tcond | Condensing saturation temperature calculated as Tamb plus condenser TD. |
| Tevap | Evaporating saturation temperature calculated as Tamb minus evaporator TD. |
| Tdis | Discharge temperature, calculated as Tcond plus discharge superheat. |
| Tco | Condenser outlet liquid temperature, calculated as Tbubble minus condenser subcool. |
| Tlro | Liquid receiver outlet temperature, a small drop below Tco in the model. |
| Teo | Evaporator outlet temperature, calculated as Tevap plus evaporator superheat. |
| Tacco | Accumulator outlet temperature, a small rise above Teo in the model. |
| Tsuc | Suction temperature at compressor inlet, derived from evaporating condition plus suction superheat. |
| Tcondairo | Condenser air outlet temperature, Tamb plus condenser split. |
| Tevapairo | Evaporator air outlet temperature, Tamb minus evaporator split. |
| TD, temperature difference | Assumed gap between air temperature and refrigerant saturation temperature in a coil. |
| SH, superheat | Degrees the vapour is above saturation temperature at a given pressure. |
| SC, subcool | Degrees the liquid is below saturation temperature at a given pressure. |
| Split | Air temperature change across a coil, used to estimate air outlet temperatures. |
| Compressor | Component that compresses low pressure vapour to high pressure vapour. |
| Condenser | Heat exchanger where refrigerant rejects heat and condenses. |
| Evaporator | Heat exchanger where refrigerant absorbs heat and evaporates. |
| Metering device | Restriction that drops pressure and controls flow into the evaporator. |
| TXV | Thermostatic expansion valve, modulating metering device. |
| CTV | Capillary tube valve, fixed restriction representation. |
| AXV | Automatic expansion valve, not simulated in the emulator logic. |
| Liquid receiver | Vessel for storing liquid refrigerant and stabilising liquid supply. |
| Accumulator | Suction side vessel that reduces risk of liquid returning to the compressor. |
| Sight glass | Viewing window used to observe liquid line condition. |
| Fin tube heat exchanger | Air coil construction used for both condenser and evaporator on the trainer. |
| Truth table | The list of valid valve combinations. The emulator runs only when a valid column is matched. |
| Valid configuration | A valve pattern that exactly matches one truth table column. |
| Emulation gate | The validation step that enables or pauses emulation based on valve configuration. |
| Tentative values | Placeholder offsets that will be tuned using observations from the physical unit. |
| kPa | Kilopascals, pressure unit used in the emulator outputs. |
| °C | Degrees Celsius, temperature unit used in the emulator outputs. |
| K | Kelvin difference, used for temperature deltas, same step size as degrees Celsius. |