# TU-100 Emulator

# Schematic

## Abbreviations:

| Acronym | Description | Acronym | Description |
| --- | --- | --- | --- |
| HP1 to HP4 | High pressure valve 1 to valve 4 | CTV | Capillary tube valve |
| LRI | Liquid receiver inlet | AXV | Automatic expansion valve |
| LRK | Liquid receiver king valve | ACI | Accumulator inlet |
| LRB | Liquid receiver bypass | ACO | Accumulator outlet |
| TXV | Thermostatic expansion valve | ACB | Accumulator bypass |

Note: AXV is not emulated.

# Digital entities

- 12 Valves (clickable on-off indications)

3 pressure indications (gauges-radial needle movement with digital display on top) with following labels:

- Condenser pressure (Pdis)-Red gauge

- Evaporator pressure (Pevap)-Red gauge

- Suction pressure (Psuc)-Blue gauge

Condenser and evaporator labels will swap at fin-tube heat exchangers if running in heating mode

- 8 temperature indications (temperature pipe clamp with digital display-see below image):

https://refcoswiss.com/en-us/produkte/temperature-clamp-for-refmate-and-tap~p2472

- Discharge (Tdis)

- Condenser outlet (Tco)

- Liquid receiver outlet (Tlro)

- Evaporator outlet (Teo)

- Accumulator outlet (Tacco)

- Suction (Tsuc)

- Ambient air (Tamb)

- Condenser air outlet (Tcondairo)

- Evaporator air outlet (Tevapairo)

Condenser and evaporator labels will swap at fin-tube heat exchangers if running in heating mode

- 2 air flow indications (digital display next to the fin-tube heat exchangers): 6 L/min (tentative value which will be revised in the next draft)

- 2 emulator selections: drop down menu-refrigerant type, slider-ambient air

# Valves configurations

Only following valve configurations whose labels are given as follows will run emulation:

- Cooling with TXV, liquid receiver and accumulator

- Heating with TXV, liquid receiver and accumulator

- Cooling with CTV and accumulator

- Heating with CTV and accumulator

- Cooling with TXV and liquid receiver

- Heating with TXV and liquid receiver

- Cooling with CTV

- Heating with CTV

Any column from the following truth table should be satisfied to make the emulation run

|  | Cool, TXV with LR and AC | Heat, TXV with LR and AC | Cool, CTV w/o LR and AC | Heat, CTV w/o LR and AC | Cool, TXV with LR and w/o AC | Heat, TXV with LR and w/o AC | Cool, CTV w/o LR and w/o AC | Heat, CTV w/o LR and w/o AC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| HP1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |
| HP2 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |
| HP3 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |
| HP4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 |
| LRI | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 |
| LRK | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 |
| LRB | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 |
| TXV | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 |
| CTV | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 |
| ACI | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |
| ACO | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 |
| ACB | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |

# Pressure temperature relationships

The gauge pressure-temperature polynomials in units of kPa as function of temperature with units of °C are given below for different refrigerants in the range of -20-70 °C:

R134a: Pdew = Pbubble = 2.087e-06*x^{4} + 0.00089072*x^{3} + 0.14797*x^{2} + 10.616*x + 191.46

Tbubble = Tdew

R290: Pdew = Pbubble = 1.4626e-06*x^{4} + 0.00074114*x^{3} + 0.16485*x^{2} + 14.499*x + 373.11

Tbubble = Tdew

R32: Pdew = Pbubble = 7.1215e-06*x^{4} + 0.0014878*x^{3} + 0.31693*x^{2} + 26.107*x + 711.64

Tbubble = Tdew

R454C:

Pdew = 6.7169e-06*x^{4} + 0.00092632*x^{3} + 0.19689*x^{2} + 15.337*x + 352.44

Pbubble = 4.7174e-07*x^{4} + 0.0010434*x^{3} + 0.21318*x^{2} + 18.288*x + 482.86 (not needed)

For Tbubble estimation, x = Pdew:

Tbubble = - 1.635e-12*x^{4} + 1.383e-08*x^{3} - 4.571e-05*x^{2} + 0.0909*x - 35.07

# Emulation logic

Assumed (will revise based on actual operation in next draft): Condenser TD = Evaporator TD = 15 K, Evaporator SH = 5 K, Suction SH = 15 K, Discharge SH = 30 K, Condenser SC = 5 K, Condenser split = Evaporator split = 5 K

Formulae:

Condenser saturation temperature (Tcond) = Condenser TD + Tamb

Condenser pressure (Pdis) = Pdew (Tcond)

Evaporator saturation temperature (Tevap) = Tamb - Evaporator TD

Evaporator pressure (Pevap) = Pdew (Tevap)

Suction pressure (Psuc) = Pdew (Tevap - 5) (5 is tentative. This value will be revised in the next draft)

Discharge (Tdis) = Tcond + Discharge SH

Condenser outlet (Tco) = Tbubble – Condenser SC

Liquid receiver outlet (Tlro) = Tco – 0.1 (0.1 is tentative. This value will be revised in the next draft)

Evaporator outlet (Teo) = Tevap + Evaporator SH

Accumulator outlet (Tacco) = Teo + 1 (1 is tentative. This value will be revised in the next draft)

Suction (Tsuc) = (Tevap – 5) + suction SH (5 is tentative. This value will be revised in the next draft)

Condenser air outlet (Tcondairo) = Tamb + Condenser split

Evaporator air outlet (Tevapairo) = Tamb – Evaporator split

# Refrigerant state visualizations

Video recording to be made while the equipment is in operation showing the observed flow in acrylic tubes and sight glass when emulation is running.